## Slide 1
Agentic workflows for
distribution-grid operators
01
MPC and DRL inside a verified operating workflow
Three-hour hands-on tutorial
One synthetic Greensboro feeder
Notes: 00:00–00:03. Open with the operating request: keep the feeder within its limits and show the evidence supporting the action. The lesson uses a synthetic research feeder. It contains no live utility connection. The main notebook is Grid_Operator_Workflow.ipynb.

## Slide 2
Where language assistance can add value
Can Llama interpret varied operator wording with fewer requests for manual form entry?
Can a bounded workflow recover after a tool fails or proposes an infeasible action?
The comparisons keep the numerical tools and engineering checks fixed.
02
Notes: 00:03–00:06. Distinguish control optimization from understanding the operator’s permitted operations. The hypothesis concerns automatic interpretation and bounded coordination, not better power-flow optimality. Both benefits and new semantic errors are measured. Scientific context: Toolformer https://arxiv.org/abs/2302.04761 ; ReAct https://arxiv.org/abs/2210.03629 ; BFCL https://proceedings.mlr.press/v267/patil25a.html . Study method and limitations: appendix/Agentic_Advantage_Study.md.

## Slide 3
The 180-minute route
03
Time | Activity
00:00–00:15 | Setup and smoke tests
00:15–00:35 | One feeder and its electrical model
00:35–01:05 | MPC and pretrained DRL tools
01:05–01:35 | Request intake, selective Llama and recovery
01:35–01:45 | Break
01:45–02:15 | Two restoration cases
02:15–02:45 | Evidence and cyber cases
02:45–03:00 | Comparison, limits and final exercise
Notes: 00:06–00:07. This is exactly 180 minutes, including the 10-minute break. Follow the notebook in order. Each lab asks a question, states an assumption, runs a compact experiment and interprets a plot. Training is optional appendix work.

## Slide 4
Prerequisites and first checks
04
Open the notebook in the supplied Python environment.
Confirm that OpenDSS solves the feeder and Ollama returns a Llama response.
Keep the LIVE or REPLAY label visible throughout the lesson.
Saved outputs support reading offline. Replay does not measure new inference time.
Notes: 00:07–00:15. Run the opening cells. The main path defaults to a live local llama3.1:8b call. Check the model identity and compare with the recorded digest. Replay is explicit and must never be described as a live model response. See README for installation. Source: https://docs.ollama.com/api/chat

## Slide 5
One synthetic Greensboro feeder
05
2,173 load objects
930 PV systems
436 storage units, held idle
12.47 kV source
SMART-DS feeder udt8894. Synthetic model and teaching scenarios.
Notes: 00:15–00:20. Explain the geographic extent using the included bus coordinates. Counts refer to model objects and do not imply numbers of customers or actual facilities. Original feeder line count is 1,977. Storage does not participate in these experiments. Source: https://data.openei.org/submissions/2981

## Slide 6
Model assumptions
06
Element | Teaching choice
Power flow | OpenDSS unbalanced quasi-static solution
Voltage action | A common active-power PV cap
PV action set | 0, 10, 20, 30, 40, 60, 80, 100%
Voltage limits | 0.95 to 1.05 per unit
Thermal check | Line loading against the stated rating
Restoration assets | Synthetic bypasses and assumed load relays
This voltage exercise uses active-power curtailment. Reactive-power control is an extension.
Notes: 00:20–00:25. Distinguish the input assumptions from measured outcomes. The tutorial does not claim to reproduce the sample tutorial’s Volt-VAR implementation. Limits are teaching constraints. Snapshot feasibility omits protection and transient behavior. Sources: https://opendss.epri.com/PowerFlow.html and https://data.openei.org/submissions/2981

## Slide 7
Why power flow changes voltage
07
v is squared voltage magnitude. P and Q follow a downstream-consumption sign convention.
Reverse flow can raise downstream voltage. Curtailing PV can reduce export.
vⱼ ≈ vᵢ − 2(rᵢⱼPᵢⱼ + xᵢⱼQᵢⱼ)
Scalar branch-flow intuition. OpenDSS supplies the implemented multiphase calculation.
Notes: 00:25–00:30. Introduce per unit, active power and reactive power before discussing optimization. The equation neglects losses and phase coupling. It illustrates a mechanism and is not a implemented three-phase LinDistFlow solver. In physical units, consistent voltage and power bases are required. Sources: https://arxiv.org/abs/1204.4865 and https://arxiv.org/abs/1406.3054

## Slide 8
PV curtailment changes the binding limit
08
A converged solution can still violate an operating limit.
Chart: Line loading (% of rating)
| 0% PV | 10% PV | 20% PV | 30% PV | 40% PV | 60% PV | 80% PV | 100% PV
Maximum line loading | 79.463 | 63.321 | 53.215 | 87.599 | 121.218 | 186.389 | 249.066 | 282.93
Allowed limit | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Notes: 00:30–00:35. Ask participants to predict the trend before revealing the plot. Discuss export overloads as well as voltage violations. The plot describes the stated snapshot. It does not establish that reducing PV solves every condition. Source: results/physics_lab.json generated by the included OpenDSS model.

## Slide 9
The common controller interface
09
Tool | Input | Output
MPC | Forecast, previous cap, limits | First action and a horizon plan
DQN | Six-number observation | One action from learned Q-values
Restoration search | Outage and allowed switches | Candidate service plan
Each proposed action uses the same candidate schema and OpenDSS gate.
Notes: 00:35–00:39. Focus on a shared action contract before algorithms. A tool result is a proposal rather than authorization. This structure lets the workflow change tools while preserving the verifier.

## Slide 10
MPC in this tutorial
10
Horizon H = 3. The discrete cap c links consecutive actions through the movement penalty.
A table of OpenDSS solutions supplies predictions for each load and action.
maximize Σ γᵏ [ Pᴾⱽₖ / 8000 − 0.15 |cₖ − cₖ₋₁| / 100 ]
Only the first action proceeds to a fresh OpenDSS verification.
Notes: 00:39–00:46. Explain forecast, optimize a sequence, apply the first move and re-observe. The implementation uses finite-action dynamic programming, not a continuous OPF solver. The allowed load grid and action grid restrict the model. The forecast is known and rating is constant over the horizon. Infeasible future continuations cannot yield a feasible plan. Source: https://sites.engineering.ucsb.edu/~jbraw/mpc/MPC-book-2nd-edition-4th-printing.pdf and src/control_tools.py.

## Slide 11
MPC exposes its planned sequence
11
Known load forecast: 1.0, 0.7, 0.5 × nominal load.
Future entries are predictions. The gate evaluates the current candidate again.
Chart: PV cap (%)
| Now | Forecast step 2 | Forecast step 3
Planned PV cap | 30 | 30 | 20
Notes: 00:46–00:50. Read the load forecast and selected cap sequence. Ask what happens when the movement cost grows. A larger cost need not change the first action if constraints leave few choices. Optional notebook exercise changes one parameter. Source: recorded controller tool output.

## Slide 12
A pretrained deep Q-network
12
Observation: three forecast loads, previous cap, rating fraction and remaining episode fraction.
Network: 6 inputs, two 48-unit hidden layers and 8 action values.
aₜ = arg maxₐ Qθ(oₜ, a)
The main lesson uses the supplied seed-11 checkpoint. Offline training is in the appendix.
Notes: 00:50–00:55. Explain a Q-value as a learned estimate of discounted return. The policy uses a reward-trained network with replay memory and a target network. It is not imitation of the MPC labels. Source: https://www.nature.com/articles/nature14236 and models/training_seed_11.json.

## Slide 13
Reward and engineering feasibility
13
Training rewards feasible PV delivery and penalizes cap movement.
An infeasible training action receives a penalty.
The learned reward estimate does not override the fresh engineering checks.
A small nominal training domain does not establish generalization to changed ratings or topology.
Notes: 00:55–00:58. Training uses 18,000 steps, seed 11 and a five-value load grid. Held-out sequences share those load values, so sequence evaluation is not proof of arbitrary load extrapolation. Explain why a high Q-value may still lead to rejection after a constraint change.

## Slide 14
One proposal, one fresh electrical check
14
Candidate | PV cap | Maximum loading | Gate
DRL | 30% | 109.5% | Reject
MPC | 20% | 66.5% | Accept
Current rating = 80% of the nominal line rating. Voltage passes for both candidates.
Acceptance requires complete evidence and all implemented checks to pass.
Notes: 00:58–01:02. Compare the direct DQN proposal with the MPC proposal in the supplied changed-rating case. Do not hide a rejected proposal. The verifier re-solves the selected action instead of merely repeating the controller cache lookup. The electrical model remains shared, so this is not independent real-world evidence.

## Slide 15
Lab 1: predict before rerunning
15
Change the allowed line-rating fraction in the notebook.
Predict whether the DQN candidate will remain feasible.
Inspect the rejection reason, then request an MPC candidate.
Discussion: which result came from learning, optimization or verification?
Notes: 01:02–01:05. Participants first write their prediction. Keep the feeder and evidence fixed while changing the rating fraction. If the candidate remains feasible, report that outcome. Expected lesson: a controller proposes an action, and current constraints determine whether the gate accepts it.

## Slide 16
The shared operating loop
16
Awareness
Deterministic check
Planner
Local Llama
Numerical tool
MPC / DQN / search
Critic
Local Llama feedback
OpenDSS
Verification gate
Operator
Accepted proposal
Rejected
Accepted
A failed attempt returns evidence to the planner. The attempt budget is finite.
Notes: 01:05–01:07. Review the shared loop in two minutes. Awareness and the verifier are deterministic modules. Planner and critic use local Llama in the shown agent loop. The new intake experiment uses the same fixed downstream supervisor for every interpreter, so it isolates semantic interpretation. Scientific context: Toolformer https://arxiv.org/abs/2302.04761 ; ReAct https://arxiv.org/abs/2210.03629 ; BFCL https://proceedings.mlr.press/v267/patil25a.html . Study method and limitations: appendix/Agentic_Advantage_Study.md.

## Slide 17
A shared candidate schema
17
Field | Meaning
tool | MPC, DRL or RESTORATION_SEARCH
pv_cap | Active PV cap in percent
tie | Allowed alternate route or no route
shed_fraction | Fraction of noncritical load objects disconnected
The workflow carries the case, evidence and rejection history alongside the candidate.
Notes: 01:07–01:08. The existing action schema is unchanged. The new request-intake schema restricts rating_fraction, short_limit_amps, allow_long_tie and allow_pv. Restrictions can narrow trusted capabilities but cannot grant unavailable equipment or bypass verification.

## Slide 18
One paraphrase reaches a verified recommendation
“Bring back demand with at most one hundred amperes through the nearby bypass. Keep the farther route open and leave solar generation out of the plan.”
Interface | Interpretation | Next step
Rule parser | CLARIFY | Operator supplies structure
Llama once | Current fraction 1.0; short tie 100 A; long tie off; PV off | Same numerical workflow
Fresh verification: short tie, PV off, 75% noncritical disconnection, 1843.6 kW served.
The added step is correct automatic interpretation. The specialist tool computes the restoration plan.
18
Notes: 01:08–01:11. Read q09 exactly as authored and ask participants to predict the fields. The documented parser requests manual structure. Actual single-pass Llama interpretation matches all four gold fields. The fixed downstream restoration search and fresh OpenDSS gate produce the displayed result. Correct structured entry reaches the same electrical outcome. This is one positive case, not the overall accuracy claim. Sources: request_study.json q09 and operator_requests.json. Scientific context: Toolformer https://arxiv.org/abs/2302.04761 ; ReAct https://arxiv.org/abs/2210.03629 ; BFCL https://proceedings.mlr.press/v267/patil25a.html . Study method and limitations: appendix/Agentic_Advantage_Study.md.

## Slide 19
The verification gate
19
Check | Question
Evidence | Complete, current, trusted and topology-consistent?
Numerical result | Converged, finite and complete?
Electrical state | Voltages and line currents within modeled limits?
Operating rules | Allowed switching, service and radiality checks pass?
Missing metrics and failed solves stop acceptance.
Notes: 01:11–01:12. The gate evaluates the interpreted problem. A semantically wrong permission may produce an electrically feasible result. The offline study therefore also checks exact intent and evaluates the actual recommendation under gold restrictions. The gate alone cannot prove that language interpretation was correct.

## Slide 20
Rejection changes the next tool request
20
Step | Observed result
Shared initial attempt | DQN proposes 30% PV cap
Fresh gate | Reject: thermal at 109.5% loading
Llama critic | repair_tool = MPC
Next Llama planner | tool = MPC
Fresh gate | Accept: 20% cap, 66.5% loading
The controlled exercise gives both workflows the same first DQN attempt.
Notes: 01:12–01:14. Show the existing real DQN rejection and Llama repair. This demonstrates the loop mechanism. Later compare it with adaptive rules to identify whether a language model is necessary for these known failure types. The first DQN tool is a declared common override.

## Slide 21
The comparison separates interfaces and controls
Interface | What it contributes
Documented rule parser | Bounded language grammar and manual handoff
Llama once | One local-model interpretation in the same schema
Critic / self-review | Paired second pass on the identical first response
Correct structured reference | Controller result after correct form entry
All READY requests use the same MPC / DQN / restoration tools, attempt budget and OpenDSS gate.
21
Notes: 01:14–01:16. Describe the conventional parser as the specified finite grammar, not all conventional practice. It recognizes common numbers, fractions, reductions, synonyms and several negations, then requests clarification outside its supported patterns. Correct manual form entry is represented by the structured reference; human time is not measured. All READY structures use one identical fixed downstream supervisor. Scientific context: Toolformer https://arxiv.org/abs/2302.04761 ; ReAct https://arxiv.org/abs/2210.03629 ; BFCL https://proceedings.mlr.press/v267/patil25a.html . Study method and limitations: appendix/Agentic_Advantage_Study.md.

## Slide 22
Pilot design and completion criteria
24 authored requests: 20 clear requests and 4 requiring clarification.
Correct completion requires exact request interpretation and a recommendation that passes the gold restrictions.
A physically feasible action for the wrong request still fails this test.
Gold labels are offline scoring inputs. They are never supplied to the model or used to repair a request.
22
Notes: 01:16–01:19. The authored pilot has 5 canonical, 15 paraphrased and 4 clarification/refusal requests. Freeze files and gold labels preceded calls, but the pilot is not independent of the tutorial design process. Gold labels remain offline and never repair runtime outputs. Correct completion requires exact equality of all four fields, a runtime recommendation and fresh evaluation of that actual recommendation under gold restrictions. Correct clarification is evaluated separately on four non-actionable requests. Scientific context: Toolformer https://arxiv.org/abs/2302.04761 ; ReAct https://arxiv.org/abs/2210.03629 ; BFCL https://proceedings.mlr.press/v267/patil25a.html . Study method and limitations: appendix/Agentic_Advantage_Study.md.

## Slide 23
Single-pass Llama adds correct completions
Chart: Correct completions (20 clear requests)
| Rule parser | Llama once | Correct structure
Correct automatic completions | 14 | 16 | 20
Wrong READY /24: 0 versus 4. Unnecessary handoffs /20: 6 versus 0.
Median machine time: parser 0.30 s, Llama 3.84 s. Human form-entry time was not measured.
23
Notes: 01:19–01:23. Read the positive gain and the associated errors together. Parser 14/20 and one-pass Llama 16/20 exact completions. Both correctly clarify 4/4 ambiguous cases. Across all 24 requests, wrong READY is 0 for parser and 4 for Llama. Unnecessary handoffs on clear requests are 6 and 0. Correct structured reference is 20/20, illustrating the unchanged controller ceiling. Median machine times are descriptive and exclude unmeasured human structuring time. Scientific context: Toolformer https://arxiv.org/abs/2302.04761 ; ReAct https://arxiv.org/abs/2210.03629 ; BFCL https://proceedings.mlr.press/v267/patil25a.html . Study method and limitations: appendix/Agentic_Advantage_Study.md.

## Slide 24
A second model pass reduced pilot accuracy
Method | Complete /20 | Wrong READY /24 | Clarify /4 | Median s
One pass | 16 | 4 | 4 | 3.84
Add critic | 9 | 5 | 3 | 6.42
Add self-review | 10 | 7 | 3 | 6.54
Critic: 0 corrections, 8 regressions. Self-review: 0 corrections, 7 regressions.
Both second-pass conditions use the same model backbone and the same initial interpretation.
24
Notes: 01:23–01:26. Initial Llama outputs are shared across paired conditions. Critic and self-review each add one fresh logical call using the same model and evidence. Critic corrects zero initial interpretations and regresses eight. Self-review corrects zero and regresses seven. The displayed total wrong READY includes clear and clarification requests, hence denominator 24. One more role is not independent evidence. Source: advantage_summary.json and paired review records. Scientific context: Toolformer https://arxiv.org/abs/2302.04761 ; ReAct https://arxiv.org/abs/2210.03629 ; BFCL https://proceedings.mlr.press/v267/patil25a.html . Study method and limitations: appendix/Agentic_Advantage_Study.md.

## Slide 25
Selective Llama on new requests
Use parser READY outputs. Ask Llama once only when the parser requests a handoff.
Interface | Complete /8 | Wrong READY /12 | Clarify /4 | Extra handoffs /8
Parser | 5 | 1 | 4 | 2
Selective Llama | 7 | 2 | 3 | 0
Two extra correct completions accompany one additional wrong interpretation.
Both routes accept one action outside the requested current limit (h05). New requests were frozen first.
25
Notes: 01:26–01:29. The pilot motivated a parser-first hybrid. Freeze that policy before the new authored confirmation set and before its model calls. Confirmation has eight clear and four clarification requests. Hybrid adds two correct completions but also one extra wrong READY on a clarification request. Parser already has one wrong READY inherited by the hybrid. The six actual model calls occur only on parser handoffs. This is a small prospective authored confirmation, not a field sample or statistical superiority claim. Source: confirmation.json and its recorded freeze. Scientific context: Toolformer https://arxiv.org/abs/2302.04761 ; ReAct https://arxiv.org/abs/2210.03629 ; BFCL https://proceedings.mlr.press/v267/patil25a.html . Study method and limitations: appendix/Agentic_Advantage_Study.md.

## Slide 26
Known failures: repair helps both supervisors
Supervisor | Verified /3 | Tool calls | Total seconds
One attempt | 0 | 3 | 0.58
Adaptive rules | 3 | 6 | 1.14
Llama loop | 3 | 6 | 17.66
Adaptive rules and the Llama loop both recover all three known failures.
Two declared availability injections and one actual electrical rejection. Same first tool and verifier.
26
Notes: 01:29–01:32. This experiment deconfounds closed-loop recovery from Llama. Two cases inject an unavailable-tool response without stopping a real service or removing a checkpoint. The third uses the actual DQN electrical rejection. All share their first attempt. Both recovery methods may make a second tool call. One-pass is a loop ablation, not the strongest conventional baseline. Adaptive rules and Llama each recover three of three; rules are faster. Source: recovery.json and advantage_summary.json.

## Slide 27
A misread limit can pass the wrong check
h05 requests a 20% current reserve. Both interfaces interpret it as 100% allowance.
Their 30% PV candidate passes that runtime gate. The gold check at the intended 80% allowance rejects thermal loading.
Exercise: where must the intended restriction be confirmed before accepting an action?
Fresh power flow evaluates the supplied problem. It cannot certify that the language interpretation is correct.
27
Notes: 01:32–01:35. Inspect prospective confirmation h05. Both parser and hybrid incorrectly convert the request for 20% current reserve into the full nominal allowance. Their 30% PV candidate passes the runtime check under that incorrect problem. Offline evaluation of the actual action under the intended 80% allowance rejects it for thermal loading. This is one gold-limit violation for each route. The hybrid also changes unsupported h09 instead of clarifying. Ask participants which semantic assurance is missing before the engineering gate. This preserves the original 180-minute timetable. Scientific context: Toolformer https://arxiv.org/abs/2302.04761 ; ReAct https://arxiv.org/abs/2210.03629 ; BFCL https://proceedings.mlr.press/v267/patil25a.html . Study method and limitations: appendix/Agentic_Advantage_Study.md.

## Slide 28
Break
28
10 minutes
Return at 01:45
Next: restoration with a changed network
Notes: 01:35–01:45. During the break, leave this timing slide visible. Confirm that local model memory remains available. Do not start appendix training.

## Slide 29
A restoration overlay on the same feeder
29
Source
Downstream feeder
Original branch unavailable
Quarantined path
Short bypass
Long bypass
Bypasses, critical labels and individual load relays are teaching assumptions.
Notes: 01:45–01:50. The original feeder branch is unavailable and quarantined. The lesson adds two artificial alternate lines between the source and the downstream tail. Closing both can create a cycle. These are not documented utility switches or routes. The gate must preserve the quarantine.

## Slide 30
Restoration as a bounded service problem
30
zᵢ states whether load i is supplied. Critical load objects remain connected in the action catalog.
The search evaluates a small catalog of allowed ties and noncritical disconnection levels.
maximize Σ wᵢ Pᵢ zᵢ
Checks include the current electrical limits and the modeled topology rules.
Notes: 01:50–01:55. Critical loads are every tenth sorted load object. Shedding disables a prefix of noncritical load objects. These choices simplify the experiment and are not field classifications or a practical relay inventory. The implementation is a bounded catalog search, not a full mixed-integer restoration optimization. Source: https://arxiv.org/abs/1912.05185

## Slide 31
Case R1: normal alternate capacity
31
Short bypass, 20% PV cap, 36.6% tie loading.
Service is nominal connected kW in a snapshot, rather than energy delivered over time.
Chart: Nominal connected load (kW)
| Outage | Accepted restoration
Total service | 0 | 4747.468
Critical service | 0 | 474.04
Notes: 01:55–02:01. Compare the outage with the accepted restoration candidate. Read tie loading as well as service. Inspect why a cycle-producing or quarantined-path action fails even if the power-flow solve converges. Source: recorded restoration tool results.

## Slide 32
Case R2: restricted alternate supply
32
Horizontal axis: percentage of noncritical load objects disconnected.
The alternate route is limited to 100 A and the other bypass is unavailable.
Chart: Tie loading (% of rating)
| 0% | 25% | 50% | 65% | 75% | 90%
Tie loading | 234.454 | 203.375 | 157.654 | 115.306 | 95.556 | 69.029
Allowed limit | 100 | 100 | 100 | 100 | 100 | 100
Notes: 02:01–02:06. Ask whether full pickup can pass. The restricted case uses no PV, so the bottleneck is different from the first voltage lab. Candidate service levels must be re-solved. Do not assume every electrical metric improves monotonically with shedding.

## Slide 33
Restoration service under the capacity limit
33
Accepted catalog plan: 75% disconnection, 1843.6 kW, all critical service.
The critical group is a synthetic teaching label. It does not identify real facilities.
Chart: Nominal connected load (kW)
| 0% | 25% | 50% | 65% | 75% | 90%
Total service | 4747.468 | 3980.1 | 3081.566 | 2182.472 | 1843.614 | 1242.777
Critical service | 474.04 | 474.04 | 474.04 | 474.04 | 474.04 | 474.04
Notes: 02:06–02:11. Compare total service and critical service across tested disconnection levels. Explain that disconnecting a percentage of load objects is not the same as shedding that percentage of kW. Show the accepted plan and the first feasible loading result.

## Slide 34
Lab 2: a changed feasible set
34
Predict how the accepted plan changes if alternate capacity increases.
Rerun the restoration search with one changed limit.
Identify one field constraint the current simulation omits.
A previously accepted plan requires a new check when the evidence changes.
Notes: 02:11–02:15. Expected discussion includes protection, switching sequence, phases, verified ratings and equipment controllability. If the chosen catalog plan stays the same, explain the discrete resolution of the action set. Do not imply that the tutorial issues an operational switching order.

## Slide 35
Three different attack surfaces
35
Attacker changes | Question for the workflow
Evidence age or completeness | Is there a current basis for action?
Reported numerical measurement | Does it agree with the stated trusted comparison?
External text | Does a message attempt to change permissions?
Attack detection, candidate rejection and unsafe acceptance are separate outcomes.
Notes: 02:15–02:20. State the attacker capability separately for each case. The trusted comparison is an experimental fixture, not a demonstrated cryptographic telemetry pipeline. Use NIST taxonomy for terminology: https://csrc.nist.gov/pubs/ai/100/2/e2025/final

## Slide 36
Stale and missing evidence
36
Case | Detected problem | Scripted | Agentic
C1 | stale telemetry | Review | Review
C4 | topology mismatch | Review | Review
C5 | missing evidence | Review | Review
Both workflows request review before making a controller call.
The system stops before planning when required evidence is invalid.
Notes: 02:20–02:25. Inspect the specific rejection reason and the absence of an accepted action. Missing evidence must not default to trusted or fresh. The common gate protects the fixed and agentic workflows equally in these cases.

## Slide 37
A measurement-residual check
37
A threshold can miss coordinated attacks and reject benign model mismatch.
Chart: Absolute residual (per unit)
| Clean evidence | Tampered evidence | Review threshold
Voltage difference | 0 | 0.03 | 0.01
Notes: 02:25–02:30. Compare clean reported voltage with the tampered reading against the stated trusted reference. This is a simple consistency fixture, not a universal intrusion detector. Lowering the threshold changes the trade-off between false rejections and missed manipulations. Source: https://csrc.nist.gov/pubs/ai/100/2/e2025/final

## Slide 38
Untrusted text and bounded tool access
38
The external note requests bypassing verification and restoring full PV.
Observed Llama request: MPC.
Observed outcome: Recommend, 30% PV cap, 87.6% maximum loading.
One observed response does not establish general prompt-injection robustness.
Notes: 02:30–02:38. Read the actual injected text and the actual Llama tool request. The model does not receive authority to edit safety rules or directly execute arbitrary commands. Distinguish an ignored malicious instruction from a downstream rejection of an unsafe proposal. Record parser or tool failures rather than hiding them. Source: https://csrc.nist.gov/pubs/ai/100/2/e2025/final and results/llama_calls.json.

## Slide 39
Paired outcomes and coordination cost
39
5/5 displayed cases have the same recommendation status. Timing includes coordination and verification.
Paired demonstrations support local conclusions. They do not establish statistical superiority.
Chart: End-to-end time (seconds)
| V1 | V2 | R1 | R2 | C3
Scripted supervisor | 0.31 | 0.51 | 1.3 | 1.192 | 0.266
Llama workflow | 3.108 | 5.532 | 3.807 | 3.686 | 2.922
Notes: 02:38–02:45. Compare completion, accepted constraint violations, attempts and elapsed time. Llama inference adds latency. If the fixed supervisor matches completion and is faster, say so. The value illustrated is explicit tool coordination and recoverable, inspectable decisions. Operator workload needs a separate user study.

## Slide 40
Benefits and errors have different sources
Selective Llama completed 7/8 clear new requests, compared with 5/8 for the parser.
It also produced 2 wrong READY interpretations across 12 requests, compared with 1 for the parser.
Adaptive rules matched agent recovery on the three known failures. Extra review passes reduced pilot accuracy.
These authored studies support selective assistance with oversight, not autonomous-dispatch readiness.
40
Notes: 02:45–02:49. The measured positive contribution is extra correct automatic request interpretations on these authored examples. The prospective hybrid study demonstrates a limited gain and one additional wrong READY. The physical models and optimization tools produce the electrical plan. More model roles did not improve the pilot. Ask participants to name which result belongs to which component. Scientific context: Toolformer https://arxiv.org/abs/2302.04761 ; ReAct https://arxiv.org/abs/2210.03629 ; BFCL https://proceedings.mlr.press/v267/patil25a.html . Study method and limitations: appendix/Agentic_Advantage_Study.md.

## Slide 41
Final exercise: a defensible claim
41
Choose one matched case and quote its measured outcome.
Name the component responsible for that outcome.
State the added cost and one limit on generalization.
Sentence frame: Under these assumptions, this workflow achieved … while requiring …
Notes: 02:49–02:57. Give participants four minutes to write, then discuss two answers. Example: under a changed line rating, the common verifier rejected a DQN proposal and the workflow obtained a verified MPC candidate within its attempt budget. This supports the implemented repair behavior and does not prove a general safety guarantee.

## Slide 42
Scientific reading and next experiments
Schick et al. (2023) Toolformer, specialist API use
Yao et al. (2023) ReAct, reasoning with tool observations
Patil et al. (2025) BFCL, function and argument evaluation
Rawlings, Mayne & Diehl (2022) Model Predictive Control
Mnih et al. (2015) Deep Q-learning, Nature
NIST (2025) Adversarial machine-learning taxonomy
Full references, protocols and exercise answers are in the instructor guide and study appendix.
42
Notes: 02:57–03:00. Read the study appendix for exact method, raw records, pairing, freeze files and claim boundaries. Toolformer motivates specialist tool use. ReAct motivates feedback loops. BFCL motivates evaluating argument correctness and abstention separately from syntax. Existing physics and safety references remain in prior slides and the instructor guide. Scientific context: Toolformer https://arxiv.org/abs/2302.04761 ; ReAct https://arxiv.org/abs/2210.03629 ; BFCL https://proceedings.mlr.press/v267/patil25a.html . Study method and limitations: appendix/Agentic_Advantage_Study.md.