## Slide 1
Agentic workflows for
distribution-grid operators
01
Voltage support, restoration and cyber-attack response
Three-hour hands-on tutorial
Greensboro feeder and small method-isolation labs
Notes: 00:00–00:03. Three-hour tutorial with exactly three core use cases: Voltage support, Restoration, and Cyber-attack response. Conventional optimization defines the engineering objective and constraints. Agent roles coordinate evidence, registered tools, bounded recovery and reporting. The frozen full-feeder workflow experiments use restricted teaching implementations. The Standard_Formulations companion isolates standard methods, with scopes stated separately.

## Slide 2
Three use cases and established methods
Core use case | Established numerical method | Agent contribution
Voltage support | Three-phase Volt/VAR OPF in receding-horizon MPC | Prepare forecasts and constraints, route tools, verify
Restoration | Mixed-integer service restoration with network constraints | Collect topology and priorities, coordinate retries
Cyber-attack response | WLS estimation, residual tests and trusted-data redispatch | Quarantine evidence, request review, explain status
The objective and engineering constraints stay the same in the conventional and agent-coordinated routes.
02
Notes: 00:03–00:07. Explain the general formulation first. The same conventional problem, solver restrictions and verification contract should apply to both supervisors in a matched experiment. Agents coordinate the engineering work. They do not invent a different optimization objective. Sources: Gan and Low (2014), https://arxiv.org/abs/1406.3054 ; Maharjan, Khambadkone and Peng (2021), https://doi.org/10.1109/TSTE.2020.3001115 ; Chen et al. (2018), https://doi.org/10.1109/TPWRS.2017.2720122 ; Wang et al., https://arxiv.org/abs/1912.05185 ; Handschin et al. (1975), https://doi.org/10.1109/T-PAS.1975.31858 ; PowerModelsDistributionStateEstimation bad-data documentation, https://electa-git.github.io/PowerModelsDistributionStateEstimation.jl/v0.4/bad_data/ ; Liu, Ning and Reiter (2009), https://reitermk.github.io/papers/2009/CCS1.pdf

## Slide 3
The 180-minute route
Time | Activity
00:00–00:15 | Setup and smoke tests
00:15–00:35 | One feeder and two physical model scopes
00:35–01:15 | Use case 1: Voltage support
01:15–01:35 | Shared agent workflow and matched comparisons
01:35–01:45 | Break
01:45–02:15 | Use case 2: Restoration
02:15–02:45 | Use case 3: Cyber-attack response
02:45–03:00 | Model limits, operator readback and final exercise
03
Notes: 00:07–00:10. Total 180 minutes: setup15, models20, voltage40, shared workflow20, break10, restoration30, cyber30, comparison15. Use one live feeder model route and the saved comparisons for the other. Open the Standard_Formulations companion for conventional-method isolation experiments.

## Slide 4
Prerequisites and first checks
Open Standard_Formulations.ipynb for the conventional-method labs.
Choose Workflow_OpenDSS.ipynb or Workflow_LinDistFlow3.ipynb for the complete agent workflow.
Run the model smoke test and local Llama check. Keep LIVE or REPLAY visible.
Use saved comparisons for the second model. Installation steps are in README.md.
04
Notes: 00:10–00:15. README.md supplies setup. Standard_Formulations.ipynb is the conventional-method companion. Workflow_OpenDSS.ipynb and Workflow_LinDistFlow3.ipynb contain the restricted complete workflow variants. Select one live route and use saved results for the second to stay within the three-hour session. Keep live/replay status visible. The independent LinDistFlow route requires no OpenDSS import.

## Slide 5
One synthetic Greensboro feeder
05
2,173 load objects
930 PV systems
436 storage units, held idle
12.47 kV source
SMART-DS feeder udt8894. Synthetic model and teaching scenarios.
Notes: 00:15–00:21. Explain the geographic extent using the included bus coordinates. Counts refer to model objects and do not imply numbers of customers or actual facilities. Original feeder line count is 1,977. Storage does not participate in these experiments. Source: https://data.openei.org/submissions/2981

## Slide 6
General models and classroom implementations
Use case | General formulation | Restricted 32-run workflow
Voltage support | Three-phase P/Q OPF with MPC | Eight active PV caps, horizon 3
Restoration | Mixed-integer topology and service optimization | Two artificial ties and a finite action catalog
Cyber-attack response | WLS, residual detection, trusted-data redispatch | Freshness, topology and aggregate voltage checks
The companion notebook isolates each conventional method.
The restricted feeder runs show orchestration behavior under their stated assumptions.
06
Notes: 00:21–00:27. Explicit scope map. The general problem statements are standard engineering formulations, not claims that the original workflow executed continuous OPF, restoration MILP or state estimation. Standard_Formulations uses numerical P/Q optimization on the Greensboro model, a reduced graph restoration MILP and a separate linear WLS example. The frozen 32-run study remains discrete active-power cap MPC, enumerated restoration catalog and aggregate min/max voltage comparison. None of those aggregate checks is WLS. See appendix/General_Optimization_Formulations.md.

## Slide 7
Two physical models and their scope
wⱼ = wᵢ − 2 Re[ conj(Dβ) Zᵢⱼ Dβ conj(Sᵢⱼ) ]
Dβ = diag(1, e⁻ʲ²π⁄³, eʲ²π⁄³) w: squared phase voltage
OpenDSS solves the nonlinear AC model of the full feeder.
Three-phase LinDistFlow propagates coupled phase voltages through the medium-voltage network.
Compare common MV quantities. LinDistFlow omits LV voltage and transformer thermal checks.
07
Notes: 00:27–00:31. Explain the lossless coupled three-phase LinDistFlow approximation. The squared voltage vector w has units V², branch power vector S has units VA, and Dβ is the diagonal balanced phase-reference matrix. The actual phase impedance matrices retain mutual terms. Branch power sums downstream load minus generation, with line-pi shunts evaluated at nominal voltage. The network has 453 MV buses, 599 node-phase values and 452 original MV lines: 380 single-phase and 72 three-phase. There are two added synthetic restoration ties. 258 primary transformer aggregations map all 2173 loads and 930 PV systems; 436 storage units remain idle. Current reconstruction uses a fixed balanced 1.03 pu source reference. LinDistFlow does not predict LV voltage or transformer thermal loading. OpenDSS includes the full feeder. Compare common MV bus-phase and branch-phase quantities, and report a separate full-feeder AC audit. Reference: Gan and Low (2014), section V, equations 12a–c, https://arxiv.org/abs/1406.3054 and data/lindistflow3_network.json.

## Slide 8
Restricted voltage lab: active PV caps
08
A converged solution can still violate an operating limit.
Chart: Line loading (% of rating)
| 0% PV | 10% PV | 20% PV | 30% PV | 40% PV | 60% PV | 80% PV | 100% PV
Maximum line loading | 79.463 | 63.321 | 53.215 | 87.599 | 121.218 | 186.389 | 249.066 | 282.93
Allowed limit | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Notes: 00:31–00:35. Ask participants to predict the trend before revealing the plot. Discuss export overloads as well as voltage violations. The plot describes the stated snapshot. It does not establish that reducing PV solves every condition. Source: results/physics_lab.json generated by the included OpenDSS model.

## Slide 9
General framework: tools and responses
Stage | Method or registered tool | Visible response
Awareness | State estimation and data checks | Trusted inputs or review reason
Planning | OPF-MPC, MILP and Llama routing | Plan and declared constraints
Execution | Solver or DQN proposal | Candidate action
Simulation | OpenDSS / 3-phase LinDistFlow | Voltages and branch currents
Verification | Declared constraints and scope | Accept or reject with reasons
Recovery | Re-solve and Llama critic | Retry or request review
Explanation | Metrics and Llama explanation | Decision and remaining limits
Acknowledgment | Local result-hash readback | Pending or recorded review
Numerical tools solve the engineering problem. Each agent response stays in the recorded trace.
09
Notes: 00:35–00:40. This is a general tool contract across the three use cases. The actual restricted trace on slide20 records a different, explicitly bounded numerical implementation. Awareness may call WLS when the measurement model is available; generic freshness and schema checks are separate. Planning uses conventional Volt/VAR OPF-MPC or restoration MILP, and trusted-data redispatch for cyber response. The Llama role proposes a strategy and explains an actual result. Execution can propose a DQN action, but verification retains the same optimization constraints and model scope.

## Slide 10
Voltage support as three-phase Volt/VAR OPF
minimize Σ [ aᵥ (|Vᵢφ| − Vref)² + aₚ (pavail − p) + aᵤ ‖Δu‖² ]
subject to F₃φ(V, p, q, d) = 0
Vmin ≤ |Vᵢφ| ≤ Vmax |Iℓφ| ≤ Imax
0 ≤ p ≤ pavail p² + q² ≤ S² u ∈ U
u contains controllable P/Q setpoints and any modeled discrete devices.
The chosen network model and device constraints determine what a feasible result means.
10
Notes: 00:40–00:48. General formulation. Variables include complex phase voltages V, controllable inverter p and q, and any included tap/capacitor states. F_3phi is the chosen three-phase power-flow equality. A typical objective penalizes voltage deviation, curtailment and control movement. The weights reconcile voltage, power and movement units and define a tradeoff. They are not universal constants. Inverter circle and capability bounds must match hardware. With full nonlinear AC physics this is generally a nonconvex OPF. A linearized convex subproblem has a narrower model scope. Sources: Gan and Low (2014), https://arxiv.org/abs/1406.3054 ; Maharjan, Khambadkone and Peng (2021), https://doi.org/10.1109/TSTE.2020.3001115

## Slide 11
Receding-horizon MPC
11
Optimize a P/Q horizon, apply its first action, update the state and solve again.
Chart: the restricted three-step active PV-cap plan from the recorded OpenDSS run.
minimize Σₖ₌₀ᴴ⁻¹ Jₖ subject to constraints across the horizon
Chart: PV cap (%)
| Now | Forecast step 2 | Forecast step 3
Planned PV cap | 30 | 30 | 20
Notes: 00:48–00:53. The general MPC problem sums stage costs J_k over a horizon with power flow, control and dynamic constraints at every step. Storage would require energy-state dynamics, while a PV-only problem couples steps through control movement and forecasts. Apply only the first optimized P/Q action and re-estimate/re-solve. The chart is the older restricted OpenDSS finite-action MPC rollout with active-power caps 30,30,20 percent. It is not a continuous Volt/VAR OPF result. Sources: Maharjan, Khambadkone and Peng (2021), https://doi.org/10.1109/TSTE.2020.3001115 ; results/labs.json.

## Slide 12
A restricted DRL execution tool
12
Observation: three forecast loads, previous cap, rating fraction and remaining episode fraction.
Network: 6 inputs, two 48-unit hidden layers and 8 action values.
aₜ = arg maxₐ Qθ(oₜ, a)
The same seed-11 AC-trained policy is used in both routes. The linear route tests policy transfer.
Notes: 00:53–00:58. Explain a Q-value as a learned estimate of discounted return. The policy uses a reward-trained network with replay memory and a target network. It is not imitation of the MPC labels. Source: https://www.nature.com/articles/nature14236 and models/training_seed_11.json.

## Slide 13
Reward and engineering feasibility
13
Training rewards feasible PV delivery and penalizes cap movement.
An infeasible training action receives a penalty.
The learned reward estimate does not override the fresh engineering checks.
A small nominal training domain does not establish generalization to changed ratings or topology.
Notes: 00:58–01:01. Training uses 18,000 steps, seed 11 and a five-value load grid. Held-out sequences share those load values, so sequence evaluation is not proof of arbitrary load extrapolation. Explain why a high Q-value may still lead to rejection after a constraint change.

## Slide 14
Restricted DQN proposal and fresh verification
14
Candidate | PV cap | Maximum loading | Gate
DRL | 30% | 109.5% | Reject
MPC | 20% | 66.5% | Accept
Current rating = 80% of the nominal line rating. Voltage passes for both candidates.
Acceptance requires complete evidence and all implemented checks to pass.
Notes: 01:01–01:05. Recorded restricted OpenDSS candidate comparison. The pretrained DQN proposes 30 percent active PV cap, and the MPC candidate is20percent. Rating is80percent of nominal. DQN109.5percent allowed current rejects, MPC66.5percent passes the stated checks. This is a policy proposal inside the workflow, not a claim that DQN replaces general OPF. Source results/labs.json.

## Slide 15
Continuous P/Q optimization on the feeder
Model / action | P (MW) | Q (MVAr) | Max V (pu) | Line (%) | Screen
OpenDSS / full PV | 7.850 | 0.000 | 1.108 | 283.0 | Fail
OpenDSS / QP point | 2.904 | 0.346 | 1.043 | 99.9 | Pass
MV linear / full PV | 7.850 | 0.000 | 1.048 | 60.8 | Pass
MV linear / QP point | 7.727 | -1.249 | 1.037 | 65.3 | Pass
MV point / AC audit | 7.727 | -1.249 | 1.087 | 288.2 | Fail
Screens use different scopes: full supplied feeder versus MV phases only.
Two shared controls, one-step sensitivity QPs and fresh validation. The result is a local feasible point.
15
Notes: 01:05–01:15. Open Standard_Formulations.ipynb. The two continuous controls share active/reactive participation over930inverters: p_i=a*S_i and q_i=b*S_i. Local sensitivity QPs use a32-side inscribed capability polygon and line search with fresh physical validation. This is a one-step snapshot method, not horizon MPC or a global AC optimum. Baseline means full available active PV with zero reactive output, not a competent optimized conventional controller. Each model optimizes its own constraint scope. The original MV full-P point was already feasible in that scope. The separate full-AC audit of the optimized MV point fails with maximum voltage1.08707pu and line loading288.237percent. Larger retained power under the MV-only model therefore does not show full-feeder feasibility. Discuss which constraint is binding, then distinguish algorithm from supervisor. Source: results/standard_formulations.json, generated 2026-09-21T14:36:51.915829+00:00. Gan and Low (2014), https://arxiv.org/abs/1406.3054

## Slide 16
The shared agent workflow
Awareness
Evidence checks
Planning
Established solver
+ Llama
Execution
Proposed action
Simulation
Chosen model
Verification
Declared constraints
Recovery
Re-solve / review
Explanation
Metrics + Llama
Acknowledgment
Operator readback
If rejected
Retry
Stop
Accepted recommendation
A stopped run still reaches explanation and operator readback. No equipment is dispatched.
16
Notes: 01:15–01:17. Shared general framework for all three use cases. Preserve the conventional objective and engineering constraints. Agents coordinate inputs, route numerical tools, evaluate returned status and explain the record. The restricted complete workflow supplies executable examples, while Standard_Formulations isolates conventional numerical methods. Accepted and stopped runs both reach explanation/readback.

## Slide 17
The shared candidate record
Record field | Content
Method and model | Solver, physical model, data version and solver status
Candidate controls | P/Q setpoints, switch states or served-load decisions
Constraint contract | Requested limits, priorities and model coverage
Verification response | Residuals, violations and declared tolerances
Trace and review | Tool observations, bounded retries and operator acknowledgment
Adapters carry the established problem into the workflow with the same objective and constraints.
17
Notes: 01:17–01:18. General interface schema, distinct from the restricted implementation schema. The executable original candidates encode tool,pv_cap,tie,shed_fraction. General continuous or mixed-integer solver adapters should instead carry the appropriate indexed controls, model identifier, explicit constraint identifiers and solver status. The operator request must be resolved before the constraint contract becomes fixed.

## Slide 18
One paraphrase reaches a verified recommendation
“Bring back demand with at most one hundred amperes through the nearby bypass. Keep the farther route open and leave solar generation out of the plan.”
Interface | Interpretation | Next step
Rule parser | CLARIFY | Operator supplies structure
Llama once | Current fraction 1.0; short tie 100 A; long tie off; PV off | Same numerical workflow
Fresh verification: short tie, PV off, 75% noncritical disconnection, 1843.6 kW served.
Restricted catalog example. Llama interprets the request and the specialist search computes the plan.
18
Notes: 01:18–01:19. Read q09 exactly as authored and ask participants to predict the fields. The documented parser requests manual structure. Actual single-pass Llama interpretation matches all four gold fields. The fixed downstream restoration search and fresh OpenDSS gate produce the displayed result. Correct structured entry reaches the same electrical outcome. This is one positive case, not the overall accuracy claim. Sources: request_study.json q09 and operator_requests.json. Scientific context: Toolformer https://arxiv.org/abs/2302.04761 ; ReAct https://arxiv.org/abs/2210.03629 ; BFCL https://proceedings.mlr.press/v267/patil25a.html . Study method and limitations: appendix/Agentic_Advantage_Study.md.

## Slide 19
Verification against the declared problem
Check | Question
Request meaning | Are the intended limits and priorities confirmed?
Evidence and solver status | Are the inputs current and the numerical result usable?
Engineering constraints | Does the candidate satisfy the specified problem?
Model scope | Which components and contingencies are covered?
Independent audit | Does a separate physical check support the recommendation?
Feasibility for a misinterpreted request still fails the intended task.
19
Notes: 01:19–01:20. General gate contract. A solver reports a candidate and status under a stated model. The workflow checks requested constraints, output completeness and model scope. Full-feeder AC audit is separate when the optimizer uses MV LinDistFlow. The restricted experiment also requires a feasible finite-action horizon and dimensionless value gap at most0.02. That additional teaching envelope is not a universal OPF safety certificate.

## Slide 20
Restricted V2 trace: both agents request review
Stage | OpenDSS response | LinDistFlow response
Awareness | PASS, residual 0.000 pu | PASS, residual 0.000 pu
Planning | 20/20/20%, MPC_ONLY | 100/100/100%, MPC_ONLY
DQN execution | 30% PV cap, Q = 2.614 | 30% PV cap, Q = 2.614
Simulation | 109.5% allowed current | 50.9% allowed current
Verification | Reject: thermal and horizon | Reject: value gap 0.620 > 0.020
Llama recovery | REVIEW | REVIEW
Explanation | REVIEW_ACTION | REVIEW_MODEL_LIMITS
Operator readback | PENDING, no accepted candidate | PENDING, no accepted candidate
Actual critic response: “DRL proposal lacks safety certificate.” Both runs stop for review.
DQN first is a declared common intervention. A model rationale cannot disable the verification gate.
20
Notes: 01:20–01:21. These are actual stage responses from the frozen matched study, run 20260920T211727Z_dbbdf6. The two planners choose MPC_ONLY, but the declared common intervention evaluates DQN first in both supervisors. The DQN is identical and returns 30%. The OpenDSS route rejects thermal loading and no feasible horizon continuation. The linear route rejects the 0.6199316 dimensionless MPC value gap. Both actual Llama critics choose REVIEW despite an available MPC plan. The fixed adaptive route completes the MPC fallback, 20% for OpenDSS and 100% for LinDistFlow, whose AC audit remains separate. The quoted critic reason is actual model output, not the engineering reason for rejection. The linear planner also claims verification is unnecessary; the gate never accepts that authority. Explanation outputs are qualitative focus fields. Readback remains PENDING until local operator action. Source: results/model_workflow.json V2 and the corresponding llama_calls.json.

## Slide 21
A fair comparison of agent coordination
Hold the objective, constraints, model, numerical tools and verification fixed.
Compare a competent fixed or adaptive supervisor with the agent-coordinated route.
Measure correct completion, errors, manual handoff and time separately.
Improved request handling is a workflow result. A numerical optimum remains a property of the stated problem.
21
Notes: 01:21–01:23. General matched-comparison contract. Use conventional or adaptive orchestration as a competent baseline with the same objective, constraints, numerical solver, data, model scope, policy proposals, budget and verification. Measure interpretation, completed authorized workflow, unnecessary handoff, wrong acceptance and machine/human effort separately. Do not infer optimization improvement from a different feasible set, solver or model. Existing interface comparisons use a bounded parser, Llama once, paired critic/self-review and correctly structured reference.

## Slide 22
Actual agent trace with the restoration MILP
Stage | Named method | Recorded response
Awareness | Scenario and scope check | PASS: six-node synthetic graph
Planning | Llama routing + HiGHS MILP | RESTORATION_MILP, solved
Execution | Binary load-pickup solution | 200 kW total, 90 kW critical
Simulation | Independent graph enumeration | Weighted objective 1010 agrees
Verification | Solver and graph checks | PASS within reduced scope
Recovery | One-attempt policy | NOT_NEEDED
Explanation | Actual Llama response | REVIEW: “review the results”
Acknowledgment | Human result review | PENDING, no dispatch
The numerical checks pass. Llama’s explanation requests REVIEW.
The fixed route solves the same MILP. The broad REVIEW wording is a protocol limitation.
22
Notes: 01:23–01:24. Recorded Llama Planning call5 selects RESTORATION_MILP for the structured limited-capacity request. The numerical routine solves the six-node MILP and returns200kW total/90kW critical. Independent enumeration agrees with weighted objective1010. Numerical verification passes. Llama Explanation call6 then chooses REVIEW, saying: The provided JSON object indicates that the numerical workflow has completed successfully, with a served load of 200 kW and a critical served load of 90 kW. The 'passed_modeled_checks' field is also true, indicating that the modeled checks have been passed. Therefore, the choice is to review the results of the numerical workflow. The broad REVIEW choice is a protocol wording limitation; do not treat it as numerical infeasibility or proof of irrational behavior. The fixed route returns the same numerical plan and MODEL_RECOMMEND. Across all8runs, both voltage backends return matching controls, while restoration and cyber agent explanations request review after passing modeled checks. There is no numerical-performance or causal-advantage claim. Source: results/standard_agent_workflow.json and results/standard_stage_20260921T143826Z_42d19a61/llama_calls.json.

## Slide 23
Single-pass Llama adds correct completions
Wrong READY /24: 0 versus 4. Unnecessary handoffs /20: 6 versus 0.
Median machine time: parser 0.30 s, Llama 3.84 s. Human form-entry time was not measured.
23
Chart: Correct completions (20 clear requests)
| Rule parser | Llama once | Correct structure
Correct automatic completions | 14 | 16 | 20
Notes: 01:24–01:26. Read the positive gain and the associated errors together. Parser 14/20 and one-pass Llama 16/20 exact completions. Both correctly clarify 4/4 ambiguous cases. Across all 24 requests, wrong READY is 0 for parser and 4 for Llama. Unnecessary handoffs on clear requests are 6 and 0. Correct structured reference is 20/20, illustrating the unchanged controller ceiling. Median machine times are descriptive and exclude unmeasured human structuring time. Scientific context: Toolformer https://arxiv.org/abs/2302.04761 ; ReAct https://arxiv.org/abs/2210.03629 ; BFCL https://proceedings.mlr.press/v267/patil25a.html . Study method and limitations: appendix/Agentic_Advantage_Study.md.

## Slide 24
A second model pass reduced pilot accuracy
Method | Complete /20 | Wrong READY /24 | Clarify /4 | Median s
One pass | 16 | 4 | 4 | 3.84
Add critic | 9 | 5 | 3 | 6.42
Add self-review | 10 | 7 | 3 | 6.54
Critic: 0 corrections, 8 regressions. Self-review: 0 corrections, 7 regressions.
Both second-pass conditions use the same model backbone and the same initial interpretation.
24
Notes: 01:26–01:27. Initial Llama outputs are shared across paired conditions. Critic and self-review each add one fresh logical call using the same model and evidence. Critic corrects zero initial interpretations and regresses eight. Self-review corrects zero and regresses seven. The displayed total wrong READY includes clear and clarification requests, hence denominator 24. One more role is not independent evidence. Source: advantage_summary.json and paired review records. Scientific context: Toolformer https://arxiv.org/abs/2302.04761 ; ReAct https://arxiv.org/abs/2210.03629 ; BFCL https://proceedings.mlr.press/v267/patil25a.html . Study method and limitations: appendix/Agentic_Advantage_Study.md.

## Slide 25
Selective Llama on new requests
Use parser READY outputs. Ask Llama once only when the parser requests a handoff.
Interface | Complete /8 | Wrong READY /12 | Clarify /4 | Extra handoffs /8
Parser | 5 | 1 | 4 | 2
Selective Llama | 7 | 2 | 3 | 0
Two extra correct completions accompany one additional wrong interpretation.
Both routes accept one action outside the requested current limit (h05). New requests were frozen first.
25
Notes: 01:27–01:29. The pilot motivated a parser-first hybrid. Freeze that policy before the new authored confirmation set and before its model calls. Confirmation has eight clear and four clarification requests. Hybrid adds two correct completions but also one extra wrong READY on a clarification request. Parser already has one wrong READY inherited by the hybrid. The six actual model calls occur only on parser handoffs. This is a small prospective authored confirmation, not a field sample or statistical superiority claim. Source: confirmation.json and its recorded freeze. Scientific context: Toolformer https://arxiv.org/abs/2302.04761 ; ReAct https://arxiv.org/abs/2210.03629 ; BFCL https://proceedings.mlr.press/v267/patil25a.html . Study method and limitations: appendix/Agentic_Advantage_Study.md.

## Slide 26
Restricted study: recovery from known failures
Supervisor | Verified /3 | Tool calls | Total seconds
One attempt | 0 | 3 | 0.58
Adaptive rules | 3 | 6 | 1.14
Llama loop | 3 | 6 | 17.66
Adaptive rules and the Llama loop both recover all three known failures.
Original OpenDSS-only loop. The staged workflow uses different prompts and recovery choices.
26
Notes: 01:29–01:31. This experiment deconfounds closed-loop recovery from Llama. Two cases inject an unavailable-tool response without stopping a real service or removing a checkpoint. The third uses the actual DQN electrical rejection. All share their first attempt. Both recovery methods may make a second tool call. One-pass is a loop ablation, not the strongest conventional baseline. Adaptive rules and Llama each recover three of three; rules are faster. Source: recovery.json and advantage_summary.json.

## Slide 27
Lab: specify the problem before solving
Choose voltage support, restoration or cyber-attack response.
Name the decision variables, objective and engineering constraints. Identify the agent’s specific coordination step.
Recorded warning: h05 requested 20% reserve. Both interfaces solved with the full current allowance.
Exercise: confirm the intended constraint, then identify the same conventional solver for both supervisors.
27
Notes: 01:31–01:35. Four-minute paired exercise. Choose exactly one core use case and identify its variables, objective, constraints and data trust assumptions. Show the recorded h05 reserve error as a reason to confirm constraints before solving. It asked for20percent reserve; both interfaces used100percent allowance. The30percent PV action passed the wrong runtime gate and failed the offline intended80percent constraint. No physical solver can certify semantic intent without a valid constraint contract.

## Slide 28
Break
28
10 minutes
Return at 01:45
Next: restoration with a changed network
Notes: 01:35–01:45. During the break, leave this timing slide visible. Confirm that local model memory remains available. Do not start appendix training.

## Slide 29
Restoration: a restricted feeder overlay
29
Source
Downstream feeder
Original branch unavailable
Quarantined path
Short bypass
Long bypass
Bypasses, critical labels and individual load relays are teaching assumptions.
Notes: 01:45–01:50. The original feeder branch is unavailable and quarantined. The lesson adds two artificial alternate lines between the source and the downstream tail. Closing both can create a cycle. These are not documented utility switches or routes. The gate must preserve the quarantine.

## Slide 30
Mixed-integer restoration
maximize Σₜ Σᵢ wᵢ Pserved,ᵢₜ Δt − λsw Σₜ Σℓ |xℓₜ − xℓ,ₜ₋₁|
zᵢₜ, xℓₜ ∈ {0,1} Pserved,ᵢₜ = Pdemand,ᵢₜ zᵢₜ
Power flow, voltage, branch capacity and inverter limits
Fault isolation and source-connected radial topology
Switching sequence, available devices and service priorities
Linear physics and polyhedral device limits yield a MILP. Other physics changes the problem class.
30
Notes: 01:50–01:58. General service-restoration formulation. z_it denotes indivisible load-block pickup, x_lt switch state and P_it served power. The visible equality enforces full pickup of each selected block. Maximize priority-weighted served energy over restoration time, optionally subtract switching cost. Faulted branches remain open, topology must connect every energized load to a source and remain a radial forest, and device/power-flow/thermal/voltage constraints apply. Connectivity plus appropriate forest constraints are needed; an edge count alone is insufficient. With linear power flow the model can be MILP. Conic physics gives MISOCP, and nonlinear AC physics generally gives MINLP. The small companion MILP is a method-isolation graph, not this full-feeder unbalanced optimization. Sources: Chen et al. (2018), https://doi.org/10.1109/TPWRS.2017.2720122 ; Wang et al., https://arxiv.org/abs/1912.05185

## Slide 31
Restricted case R1: normal alternate capacity
31
Short bypass, 20% PV cap, 36.6% tie loading.
Service is nominal connected kW in a snapshot, rather than energy delivered over time.
Chart: Nominal connected load (kW)
| Outage | Accepted restoration
Total service | 0 | 4747.468
Critical service | 0 | 474.04
Notes: 01:58–02:02. Compare the outage with the accepted restoration candidate. Read tie loading as well as service. Inspect why a cycle-producing or quarantined-path action fails even if the power-flow solve converges. Source: recorded restoration tool results.

## Slide 32
Restricted case R2: limited alternate supply
32
Horizontal axis: percentage of noncritical load objects disconnected.
The alternate route is limited to 100 A and the other bypass is unavailable.
Chart: Tie loading (% of rating)
| 0% | 25% | 50% | 65% | 75% | 90%
Tie loading | 234.454 | 203.375 | 157.654 | 115.306 | 95.556 | 69.029
Allowed limit | 100 | 100 | 100 | 100 | 100 | 100
Notes: 02:02–02:06. Ask whether full pickup can pass. The restricted case uses no PV, so the bottleneck is different from the first voltage lab. Candidate service levels must be re-solved. Do not assume every electrical metric improves monotonically with shedding.

## Slide 33
Restoration MILP on a small teaching network
Chart: Served load (kW)
| Normal tie capacity | Limited tie capacity
Total served | 250 | 200
Critical served | 90 | 90
MILP and exhaustive enumeration agree on the weighted service optimum in both cases.
Six-node graph with active-power transport limits. It omits AC voltage, reactive power and protection sequencing.
33
Notes: 02:06–02:12. The companion uses six explicitly synthetic nodes and seven candidate branches. Binary served-load, energized-node and branch decisions combine with single-commodity source connectivity, radial edge count and active-power transport constraints. SciPy milp/HiGHS maximizes priority-weighted pickup. The second objective preserves optimal weighted service and minimizes energized branches with an index tie-break, not physical switching operations. Exhaustive enumeration agrees on the primary objective in both capacity cases, even if an equally optimal tree differs. This method-isolation graph is separate from the Greensboro fault overlay. Normal priority-weighted objective1060, limited1010. Source: results/standard_formulations.json, generated 2026-09-21T14:36:51.915829+00:00. Chen et al. (2018), https://doi.org/10.1109/TPWRS.2017.2720122 ; Wang et al., https://arxiv.org/abs/1912.05185

## Slide 34
Operator review and acknowledgment
Inspect the action, current limit and separate AC audit.
Read each stage’s method and response before confirming the three statements.
Record review of this result. A different result requires a new acknowledgment.
Recorded OpenDSS V1. Review is pending.
No equipment command follows.
34
Notes: 02:12–02:15. Open Operator_Dashboard.html and orient the audience using this actual captured V1 OpenDSS review. The pending form requires a name or training identifier and three readbacks. Next select R2 and compare both prediction models for the capacity-limited restoration case. Selecting a recorded run does not call Llama again. Acknowledgment is local and bound to the exact result and audit identity. It is neither verified human comprehension, utility-operator authentication nor dispatch authorization. The final exercise returns to this form so each participant can record their own review. The example remains PENDING at capture. Source: Operator_Dashboard.html and figures/operator_dashboard_readback.png.

## Slide 35
Cyber-attack response: WLS estimation
z = h(x) + e e ~ N(0, R)
x̂ = arg minₓ [z − h(x)]ᵀ R⁻¹ [z − h(x)]
r = z − h(x̂) J = rᵀ R⁻¹ r
Alert when J > χ²ₘ₋ₙ,₁₋α under the stated statistical assumptions.
m measurements, n estimated state variables. Observability and measurement covariance matter.
35
Notes: 02:15–02:23. General measurement model z=h(x)+e with covariance R and locally observable state x. WLS minimizes the weighted squared residual. For a full-rank linear Gaussian model the minimized statistic is chi-square with m-n degrees of freedom, with n free identifiable states. The nonlinear linearized version is approximate. Nonlinear estimation, pseudo-measurement errors and model mismatch can alter calibration. The new companion example is linear WLS on a small teaching system. The original feeder awareness compares aggregate min/max voltage and is not WLS. Sources: Handschin et al. (1975), https://doi.org/10.1109/T-PAS.1975.31858 ; PowerModelsDistributionStateEstimation bad-data documentation, https://electa-git.github.io/PowerModelsDistributionStateEstimation.jl/v0.4/bad_data/

## Slide 36
Detection and trusted-data redispatch
Normalized residual: rn,ᵢ = |rᵢ| / √Ωᵢᵢ
Investigate the suspect channel and preserve an observable trusted subset.
Re-estimate the state, then solve constrained redispatch using trusted inputs.
Hold for review when trust or observability is insufficient.
A numerical residual flags inconsistency. Additional evidence is needed to attribute an attack.
36
Notes: 02:23–02:30. After a global WLS residual alarm, a largest normalized residual may identify a suspect measurement, using Omega=R-H(H^T R^-1 H)^-1H^T in the linear observable case. Removal is conditional on observability and trust; it is not guaranteed cyber attribution. Re-estimate using independently justified trusted measurements. Solve the same conventional OPF/dispatch objective and constraints with trusted state/uncertainty. If trustworthy observability is insufficient, hold or escalate for operator review. Do not substitute a residual pass for security. Sources: Handschin et al. (1975), https://doi.org/10.1109/T-PAS.1975.31858 ; PowerModelsDistributionStateEstimation bad-data documentation, https://electa-git.github.io/PowerModelsDistributionStateEstimation.jl/v0.4/bad_data/ ; Liu, Ning and Reiter (2009), https://reitermk.github.io/papers/2009/CCS1.pdf

## Slide 37
WLS alarms and a coordinated false-data case
Chart: Statistic / alarm threshold
| Nominal noise | Isolated corruption | Coordinated Hc
WLS statistic / threshold | 0.2599 | 18.394 | 0.2599
Alarm boundary | 1 | 1 | 1
Stealth: no alarm and 1 toy-network overload. Trusted recovery: 0 overloads.
Four-bus DC example. Recovery assumes independent trustworthy measurements with no residual redundancy.
37
Notes: 02:30–02:38. Four-bus DC teaching model with8measurements and3free angle states. Seed11noise follows the stated covariance. The chart shows J divided by the99percent chi-square threshold,15.0862724694, with5degrees of freedom. Nominal J3.92022169, isolated corruption J277.4974469, stealth J3.92022169. The largest normalized residual identifies the intentionally corrupted channel1 for this realization. The stealth vector a=Hc preserves residuals but shifts the estimate and leads to one offline true toy-model overload with the untrusted zero-injection proposal. A separately assumed protected3-angle data set supports redispatch with no toy-model overload. This exactly determined recovery has zero residual degrees of freedom and no chi-square detection claim. Protected measurements are an explicit trust assumption, not implemented authentication. Source: results/standard_formulations.json, generated 2026-09-21T14:36:51.915829+00:00. Handschin et al. (1975), https://doi.org/10.1109/T-PAS.1975.31858 ; Liu, Ning and Reiter (2009), https://reitermk.github.io/papers/2009/CCS1.pdf

## Slide 38
Stealth FDI and untrusted instructions
Linear-model stealth: a = Hc preserves the WLS residual
A passing residual test cannot rule out coordinated false-data injection.
External text cannot change the registered tools or the engineering verification contract.
Recorded restricted text-injection case: MPC, 30% PV cap, 87.6% loading.
One observed language-model response does not establish general prompt-injection robustness.
38
Notes: 02:38–02:45. Separate attack surfaces inside the single cyber-attack-response use case. In the linear model z=Hx+e, an attacker who can add a=Hc changes the estimate byc while leaving the residual unchanged. Feasible attack support depends on access to measurement channels and system knowledge. Trusted redundancy and independent checks matter. Separately, natural-language instructions in external data should not change registered tool permissions or bypass verification. The original restricted prompt-injection run requested MPC and returned30percent PV,87.6percent allowed loading. It does not establish general prompt-injection robustness. Source: Liu, Ning and Reiter (2009), https://reitermk.github.io/papers/2009/CCS1.pdf ; results/labs.json.

## Slide 39
Restricted 32-run model and supervisor study
Model / supervisor | Issued /8 | AC pass / issued | Median s | Llama calls
OpenDSS / fixed | 5 | 5 / 5 | 0.34 | 0
OpenDSS / agentic | 4 | 4 / 4 | 6.63 | 13
LinDistFlow / fixed | 6 | 2 / 6 | 0.14 | 0
LinDistFlow / agentic | 5 | 2 / 5 | 5.79 | 13
A correct hold also prevents a recommendation. These counts are not accuracy rates.
32 fixed-order runs. Timing excludes model-table setup and the separate AC audits.
39
Notes: 02:45–02:49. Eight declared cases per condition, two backends and two supervisors, 32 workflow runs and 26 actual Llama calls. This is a fixed-order local batch, not a statistical accuracy or speed study. Recommendation counts are model-scoped and include only issued candidates. Appropriate reviews, including C1 stale evidence and C2 biased aggregate sensors, reduce those counts. The AC-pass denominator is issued recommendations, not all eight cases. OpenDSS fixed repairs V2; its agentic critic requests review. The linear fixed route issues six recommendations and the agentic route five, but only R1 and R2 pass the full-feeder AC audit in each. Median workflow time excludes each 40-solve setup table and the offline AC audit. The original policy weights, action catalog, objective, restrictions and declared cases are shared; each backend generates its own transparent synthetic awareness values. Source: results/model_comparison.json and model_workflow.json.

## Slide 40
MV error and omitted LV constraints
V1, V3 and C3 fail the full AC audit only at omitted LV elements.
Linear agentic recommendations only. Each error compares 599 common MV node-phase values.
40
Chart: Maximum MV voltage error (pu)
| V1 | V3 | R1 | R2 | C3
Maximum voltage error | 0.0017276 | 0.00050137 | 0.00079598 | 0.00041954 | 0.0017276
Notes: 02:49–02:53. These five bars represent issued LinDistFlow recommendations from the agentic route, evaluated at the identical action in OpenDSS. Each compares 599 common MV node-phase voltage values. No missing or reviewed case has been plotted as a zero error. Maximum MV error ranges from 0.000419545 to 0.001727645 pu. The full AC audit fails V1, V3 and C3 because of LV-only voltage/current violations. There are zero violating MV buses and MV lines for those recommendations. For V1, 23 LV buses violate voltage and 10 LV lines violate current, whereas its common-MV approximation error remains small. R1 and R2 pass the audit. The AC audit does not silently repair the linear plan. The scope difference must accompany any claimed gain in speed or retained PV. Sources: results/model_comparison.json and Gan & Low (2014), https://arxiv.org/abs/1406.3054 .

## Slide 41
Final exercise: review one recorded result
Choose one recorded case and inspect every stage response.
Compare the model recommendation with the separate AC audit, then complete the local dashboard readback.
Identify the conventional formulation, the agent’s contribution and one remaining limit.
Acknowledgment records review of that exact result. It does not operate equipment.
41
Notes: 02:53–02:57. Open Operator_Dashboard.html and select one model, supervisor and case. Inspect all named methods and responses. Read any AC audit separately from model acceptance. Participants should complete the local readback themselves only after reviewing the action, current restriction, scope and remaining risks. Do not fabricate or imply a human acknowledgment from a script or saved study row. The interaction records review and issues no physical dispatch. Give each participant time to formulate a measured claim and one limit.

## Slide 42
Scientific reading for the three use cases
Gan & Low (2014) Coupled multiphase power-flow approximation
Maharjan et al. (2021) Distribution voltage control using MPC
Chen et al. (2018) Unbalanced sequential restoration optimization
Wang et al. Radiality and source connectivity constraints
Handschin et al. (1975) WLS state estimation and residual tests
Liu, Ning & Reiter (2009) False-data injection and residual limits
Yao et al. (2023), Schick et al. (2023) Reasoning and tool use
Full equations, primary references and assumptions appear in General_Optimization_Formulations.md.
42
Notes: 02:57–03:00. Primary references: Gan and Low (2014), https://arxiv.org/abs/1406.3054 ; Maharjan, Khambadkone and Peng (2021), https://doi.org/10.1109/TSTE.2020.3001115 ; Chen et al. (2018), https://doi.org/10.1109/TPWRS.2017.2720122 ; Wang et al., https://arxiv.org/abs/1912.05185 ; Handschin et al. (1975), https://doi.org/10.1109/T-PAS.1975.31858 ; PowerModelsDistributionStateEstimation bad-data documentation, https://electa-git.github.io/PowerModelsDistributionStateEstimation.jl/v0.4/bad_data/ ; Liu, Ning and Reiter (2009), https://reitermk.github.io/papers/2009/CCS1.pdf ; Rawlings, Mayne and Diehl, Model Predictive Control https://sites.engineering.ucsb.edu/~jbraw/mpc/MPC-book-2nd-edition-4th-printing.pdf ; Mnih et al. (2015), https://www.nature.com/articles/nature14236 ; Yao et al. (2023), https://arxiv.org/abs/2210.03629 ; Schick et al. (2023), https://arxiv.org/abs/2302.04761 . General_Optimization_Formulations.md provides the complete equations and assumptions. The experiments illustrate, rather than validate every condition of, the cited methods.