## Slide 1
Agentic AI for grid operators
01
A focused Greensboro study
Voltage control, restoration and cyber-physical screening
IEEE SmartGridComm 2026 tutorial companion
Executed synthetic-network simulations with an optional live LLM extension
Notes: Based on the user-supplied IEEE SmartGridComm 2026 tutorial proposal by Alaa Selim, Mohamad Chehade and Mahmoud Abdelaal. This companion is a worked study, not a claim of conference acceptance.

## Slide 2
Study boundary
02
One substation area: uhs20_1247 in SMART-DS Greensboro
Voltage: udt8894 feeder, with 2,173 modeled loads and 930 PV systems
Restoration: retain three local feeders to model the alternate tie source
Synthetic assets and study conditions, with original data included
This study covers a bounded model area rather than the full city
Notes: Network provenance: https://data.openei.org/submissions/2981 . Local subset: SMARTDS_GSO_solar_extreme_batt_high_peak_opendss/uhs20_1247. No named real utility service territory is asserted.

## Slide 3
Agent roles and evidence
03
Role | Output | Advantage
Awareness | State and target catalog | Fewer unsupported assumptions
Planning | Structured candidate | Repeatable action proposal
Simulation | Physical response | Visible side effects
Verification | Pass/fail and reasons | Explicit rejection barrier
Optimizer | Revised, scored action | Feedback-guided improvement
The operator reviews the resulting recommendation and supporting evidence
Notes: Proposal sections 2–3 define these bounded roles. Notebook section 1 gives input/output contracts. Simulation is deterministic; only planning and critique optionally use a live LLM.

## Slide 4
Workflow and implementation
04
Awareness supplies a state summary to the planning agent
Each proposal enters simulation and the verification gate
Rejected proposals return reasons to the optimizer for repair
Passing actions enter simulated acceptance and operator review
The notebook displays the actual agent trace and candidate evaluation ledger
Notes: Notebook sections 1 and 3. Existing LangGraph nodes are initialize, plan, verify, repair, accept and finalize. The verify node contains simulation and verification. Accept updates simulated state only.

## Slide 5
Execution modes
05
Mode | What executes | What it establishes
Default | Deterministic proposals OpenDSS + LangGraph | Reproducible workflow and engineering safeguards
Optional live LLM | Bounded JSON planning Scored feedback + re-evaluation | A model experiment to run under the same constraints
A multi-agent architecture separates responsibilities.
It does not require an LLM for every role.
Notes: Notebook sections 0 and 5. No live model calls were made to produce the reported primary results. The optional interface uses an installed model selected through OLLAMA_MODEL.

## Slide 6
Lab 1: voltage control
06
Extreme-solar snapshot on the udt8894 leaf feeder
Allowed action: a common real-power cap for 930 existing PV systems
Criteria: 0.95–1.05 pu voltage and line loading at or below 100%
Objective: retain a higher PV cap after all checks pass
A teaching action family. Reactive-power optimization and energy scheduling remain extensions
Notes: Computed evidence: results/study_summary.json in the companion bundle. Fresh deterministic OpenDSS runs, September 19, 2026. Synthetic SMART-DS model. Notebook section 2. Cap means percent of rated PV Pmpp, not measured energy curtailment. Existing inverter ratings remain unchanged. Control mode is off.

## Slide 7
Voltage clearance alone misses thermal violations
07
Chart: Count
| Baseline | 40% cap | 33.125% cap
Voltage-violation buses | 23 | 0 | 0
Overloaded lines | 10 | 6 | 0
At a 40% cap, the voltage test passes but six lines still exceed their modeled ratings
Notes: Computed evidence: results/study_summary.json in the companion bundle. Fresh deterministic OpenDSS runs, September 19, 2026. Synthetic SMART-DS model. Rows are the baseline, initial 40% cap and selected refined cap. Bus violations use the tutorial band. Overloaded lines exceed modeled normal ratings.

## Slide 8
Verifier feedback repairs the proposal
08
33.125%
Selected common PV cap
0 voltage violations
0 overloaded lines
4,747.5 kW nominal load served
The optimizer tests a 20% repair, then refines toward a higher feasible cap. Each proposal gets a fresh solve.
Nine candidate solves. The cap is a Pmpp setting, not a percentage of energy saved
Notes: Computed evidence: results/study_summary.json in the companion bundle. Fresh deterministic OpenDSS runs, September 19, 2026. Synthetic SMART-DS model. Notebook optimizer_agent uses one repair probe and five midpoint probes. Together with three initial candidates, this uses nine candidate solves. No global optimality claim.

## Slide 9
Ablation: contribution of verification and repair
09
Workflow | Result | Candidate solves
Planner only | 80% cap still violates limits | 1
Planner + verifier | All initial proposals rejected | 3
Planner + verifier + repair | 33.125% cap passes snapshot checks | 9
This isolates workflow behavior. It does not measure LLM superiority or operator time savings
Notes: Computed evidence: results/study_summary.json in the companion bundle. Fresh deterministic OpenDSS runs, September 19, 2026. Synthetic SMART-DS model. The teaching ablation intentionally has unequal solve counts. It is not a matched-budget optimizer benchmark. Verifier-only makes no recommendation and retains the baseline.

## Slide 10
Lab 2: outage and coordinated restoration
10
Quarantine the faulted incoming line to udt8894
Test the approved alternate tie inside the substation area
Compare blind pickup with coordinated storage charging
Use watch-line feedback to refine the storage-fleet setpoint
Critical-load labels are unavailable. The reported restoration metric uses equal-weight nominal kW
Notes: Computed evidence: results/study_summary.json in the companion bundle. Fresh deterministic OpenDSS runs, September 19, 2026. Synthetic SMART-DS model. Notebook section 3. Fault: l(r:udt8894-uhs20_1247)_disconnect. Tie: elbswitch(r:udt8894-udt9916)u_82773. Watch line: recloser_disswitch(r:udt5179-udt6452)u_85430.

## Slide 11
Blind pickup creates a new watch-line overload
11
Chart: % of normal rating
| Pre-outage | Tie only | Tie + 41% charge
Watch-line loading | 48.6 | 138.8 | 99.3
100% is the modeled rating. Charging absorbs surplus in this particular solar-rich snapshot
Notes: Computed evidence: results/study_summary.json in the companion bundle. Fresh deterministic OpenDSS runs, September 19, 2026. Synthetic SMART-DS model. Static canonical states. The 41% charging case is a fixed positive control, separate from the adaptive optimizer result on the next slide. The 100% reference is the modeled normal rating.

## Slide 12
Restoration improves service, with limits remaining
12
4.747 MW
Nominal load restored after the outage
Adaptive fleet charge: 40.8%
Final watch-line loading: 99.46%
18 voltage-violation buses and 57 overloaded lines remain elsewhere. Relative improvement is not absolute clearance
Notes: Computed evidence: results/study_summary.json in the companion bundle. Fresh deterministic OpenDSS runs, September 19, 2026. Synthetic SMART-DS model. Adaptive deterministic run, 15 candidate solves. Relative certificate uses the pre-contingency envelope. Existing violations mean this does not establish absolute feasibility.

## Slide 13
Lab 3: cyber-physical screening
13
Screening layer | Controlled test
Schema and catalog | Unknown action or device, forbidden source edit
Telemetry and topology | Stale snapshot, revoked trust, fingerprint mismatch
Target quarantine | Attempt to close the faulted line
Actuation and physics | Readback faults and thermally regressive pickup
Software injections only. Trust flags are inputs, not a complete authentication system
Notes: Computed evidence: results/study_summary.json in the companion bundle. Fresh deterministic OpenDSS runs, September 19, 2026. Synthetic SMART-DS model. Notebook section 4 and run_tii_fault_injection.py. Ten deliberately designed negative controls and one positive control. Actuation faults mock readback. Other simulated cases use fresh OpenDSS solves.

## Slide 14
All designed negative controls were rejected
14
10 / 10
Negative controls rejected
7 rejected before simulation
3 rejected after simulation
1 positive control accepted
Zero unsafe simulated commitments in this small suite. No real-world attack detection rate is claimed
Notes: Computed evidence: results/study_summary.json in the companion bundle. Fresh deterministic OpenDSS runs, September 19, 2026. Synthetic SMART-DS model. cyber_summary: 10 hazard cases detected, 1 positive control accepted, 0 false rejects, 0 unsafe simulated commits. This is not a population estimate of detection performance.

## Slide 15
What the study demonstrates
15
Step | Observed contribution
Awareness | Uses exact model targets and state evidence
Simulation | Exposes the thermal cost of voltage and pickup actions
Verification | Blocks infeasible or untrusted proposals
Refinement | Finds a feasible PV cap and repairs restoration loading
Operator review | Retains the action, checks and rejection history
Measured: simulated behavior. Not measured: operator time saved or live LLM performance
Notes: Computed evidence and proposal alignment. Separation of responsibilities is observable in the notebook traces. Benefits to field operations remain to be measured.

## Slide 16
Research comparison and deployment gaps
16
Compare deterministic search, OPF and LLM variants at matched budgets
Repeat across operating points, outages, seeds and model families
Add critical-load labels, battery duration and switching-sequence checks
Validate radiality, transformer limits and protection coordination
Report residual violations, physical writes, solver calls, runtime and uncertainty alongside restoration
Notes: Notebook sections 3–6. Scope caveats also appear in the bundled GridGuard implementation. No empirical claim of LLM performance superiority is made.

## Slide 17
Three-hour tutorial plan
17
Topic | Minutes
Motivation and multi-agent workflow | 45
Open-weight models and optimizer patterns | 40
Voltage-control lab | 25
Restoration lab | 25
Cyber-physical lab | 25
Discussion | 20
Participants leave with the notebook, model subset, candidate traces and editable presentation
Notes: Timing follows the supplied proposal section 5 and sums to 180 minutes. Notebook labs are ordered voltage, restoration, then cyber.

## Slide 18
Companion materials and sources
18
Executed notebook with visible results and agent handoffs
Portable model subset and installation instructions
Machine-readable evidence and raw candidate ledgers
Optional live Llama or Qwen planning through an installed Ollama model
Network source: OEDI SMART-DS dataset 2981. Full attribution and study limitations appear in the notebook
Notes: Primary sources: supplied tutorial proposal, sections 2–5; https://data.openei.org/submissions/2981 . Evidence: results/study_summary.json, results/voltage_candidates.csv, results/restoration_states.csv, results/cyber_trials.csv and raw LangGraph ledgers in the delivered bundle.