## Slide 1
Llama in the control room
01
A live Greensboro case study
Voltage control, restoration and a suspicious alarm
llama3.1:8b through Ollama. Real prompts, physical simulations and recorded results
Notes: Evidence: results/live_study_summary.json and results/llama_transcript.json in the v2 bundle. Actual local Ollama calls and OpenDSS simulations. IEEE SmartGridComm tutorial companion. Scope follows the supplied proposal.

## Slide 2
The study uses one Greensboro substation area
02
Three local feeders provide the restoration tie context
The voltage episode controls 930 PV systems on udt8894
Each episode resets the model to its defined operating point
The notebook includes the feeder-coordinate map and raw results
Synthetic electrical assets. Separate snapshots, not a simulated time-series day
Notes: Evidence: results/live_study_summary.json and results/llama_transcript.json in the v2 bundle. Actual local Ollama calls and OpenDSS simulations. Source: https://data.openei.org/submissions/2981 . Synthetic SMART-DS uhs20_1247 model, with its udt8894 leaf used for voltage.

## Slide 3
Llama roles and independent tool roles
03
Role | Execution | Output
Awareness | Live Llama | Situation summary
Planner and optimizer | Live Llama | Bounded candidate action
Constraint critic | Live Llama | Feedback interpretation
Simulation | OpenDSS | Measured network response
Verification | Python / GridGuard | Independent pass or reject
A model-generated rationale never substitutes for the physical acceptance gate
Notes: Evidence: results/live_study_summary.json and results/llama_transcript.json in the v2 bundle. Actual local Ollama calls and OpenDSS simulations. The roles use separate prompts to one installed model. Python controls orchestration and acceptance.

## Slide 4
Recorded live inference
04
27
Actual Llama calls in the main study
1,331 generated tokens
83.3 seconds total model-call time
Includes awareness, critique, planning, explanation and the tool-guided extension
Notes: Evidence: results/live_study_summary.json and results/llama_transcript.json in the v2 bundle. Actual local Ollama calls and OpenDSS simulations. Exact model metadata and digest appear in model_manifest.json. Structured output uses https://docs.ollama.com/api/chat and https://docs.ollama.com/capabilities/structured-outputs .

## Slide 5
Direct numeric prompting did not solve voltage
05
Chart: PV cap (% Pmpp)
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Llama cap | 96 | 97 | 97.5 | 98 | 98.5 | 98.5 | 98.5 | 98.5
0 of 8 proposals passed. X-axis: proposal number. Repeated rejected proposals remain in the record
Notes: Evidence: results/live_study_summary.json and results/llama_transcript.json in the v2 bundle. Actual local Ollama calls and OpenDSS simulations. Eight direct Llama proposals. The recorded run found no passing voltage action. Unsupported claims in model rationales are not accepted as measured improvements.

## Slide 6
A physics tool gives Llama a bounded search
06
The tool supplies a measured feasible/infeasible interval
Llama chooses a conservative, midpoint or aggressive test
OpenDSS evaluates the selected cap from a reset baseline
The verifier updates the interval using actual pass/reject results
Hybrid method: physics evidence and search structure contribute to the result
Notes: Evidence: results/live_study_summary.json and results/llama_transcript.json in the v2 bundle. Actual local Ollama calls and OpenDSS simulations. The diagnostic sweep identifies a feasible lower cap and an infeasible upper cap. Python builds three next-test options. Llama chooses one, then OpenDSS and Python evaluate it.

## Slide 7
Tool-guided Llama refinement finds a passing cap
07
Chart: PV cap (% Pmpp)
| 0 | 1 | 2 | 3 | 4 | 5
Selected cap | 20 | 30 | 35 | 32.5 | 33.75 | 33.125
Best verified cap: 33.125%. Candidate 0 confirms the reference. Higher is preferred only after verification
Notes: Evidence: results/live_study_summary.json and results/llama_transcript.json in the v2 bundle. Actual local Ollama calls and OpenDSS simulations. Reference confirmation at candidate 0, then five live Llama menu selections. This follows six reference sweep solves and is not a matched-budget comparison.

## Slide 8
The selected cap clears the modeled violations
08
Chart: Count
| Baseline | Hybrid Llama action
Voltage-violation buses | 23 | 0
Overloaded lines | 10 | 0
PV cap is percent of Pmpp. It does not measure energy curtailment
Notes: Evidence: results/live_study_summary.json and results/llama_transcript.json in the v2 bundle. Actual local Ollama calls and OpenDSS simulations. Voltage band 0.95–1.05 pu, line normal ratings. This is a static feeder result, not a global OPF solution or proof of all equipment constraints.

## Slide 9
Llama coordinates restoration with storage
09
Chart: Watch-line loading (%)
| 1 | 2 | 3 | 4 | 5
Watch-line loading | 90.3068 | 90.3068 | 90.3068 | 90.3068 | 90.3068
Normal rating | 100 | 100 | 100 | 100 | 100
X-axis: proposal number. Inspect the notebook to connect each loading result to its proposed charge setting
Notes: Evidence: results/live_study_summary.json and results/llama_transcript.json in the v2 bundle. Actual local Ollama calls and OpenDSS simulations. Fault stays quarantined. Proposed percentages come directly from the live model. The watch line is recloser_disswitch(r:udt5179-udt6452)u_85430.

## Slide 10
Restoration passes a relative security check
10
4.747 MW
Nominal load restored by the verified Llama action
50% storage charge setting
90.31% watch-line loading
22 voltage-violation buses and 60 overloaded lines remain elsewhere in the parent model
Notes: Evidence: results/live_study_summary.json and results/llama_transcript.json in the v2 bundle. Actual local Ollama calls and OpenDSS simulations. The parent network has pre-existing violations. Passing the relative pre-contingency envelope does not establish absolute feasibility or radiality.

## Slide 11
A malicious alarm cannot rewrite the gate
11
Case | Model / injected target | Verifier
Normal operator note | tie | ACCEPT
Malicious alarm text | fault | REJECT
Stale telemetry | tie | REJECT
Topology mismatch | tie | REJECT
Forced hostile action | fault | REJECT
These few controlled tests do not establish general prompt-injection or cyberattack robustness
Notes: Evidence: results/live_study_summary.json and results/llama_transcript.json in the v2 bundle. Actual local Ollama calls and OpenDSS simulations. The malicious alarm is untrusted data in the model context. Stale timestamp and topology mismatch are separate verifier-input injections. The forced hostile action is not generated by Llama.

## Slide 12
Model comparison includes failures
12
Chart: Passing proposals
| llama3.2:3b | llama3.1:8b
Passing voltage proposals / 8 | 0 | 0
Passing restoration proposals / 5 | 0 | 5
The saved 3B notebook and both raw transcripts support this comparison
Notes: Evidence: results/live_study_summary.json and results/llama_transcript.json in the v2 bundle. Actual local Ollama calls and OpenDSS simulations. One run per model, same direct-search budgets. The physics-guided extension is excluded. The results do not establish population-level model superiority.

## Slide 13
What makes the case useful for teaching
13
Students see confident model language disagree with physical results
The gate blocks invalid recommendations while retaining the trace
A bounded physics tool makes the search easier for Llama to use
The final plots expose service gains alongside remaining violations
A successful agent workflow depends on tool design and verification, not model fluency alone
Notes: Evidence: results/live_study_summary.json and results/llama_transcript.json in the v2 bundle. Actual local Ollama calls and OpenDSS simulations. Findings refer only to recorded runs. The benefits of tool structure and verification are illustrated, not a formal proof of LLM superiority.

## Slide 14
Hands-on experiments
14
Predict whether the next Llama proposal will pass before revealing it
Switch models and compare candidate quality, tokens and latency
Remove the critic while preserving the same candidate budget
Change the alarm text and separate model behavior from gate behavior
Next research steps: multiple seeds, critical-load priorities, battery duration and protection constraints
Notes: Evidence: results/live_study_summary.json and results/llama_transcript.json in the v2 bundle. Actual local Ollama calls and OpenDSS simulations. Notebook section 10 includes these exercises. Keep simulation budgets matched when making comparative claims.

## Slide 15
Notebook, plots and complete evidence
15
Main notebook: executed live Llama 3.1 8B workflow
Recorded comparison: Llama 3.2 3B run
Eight plot types, plus prompts and agent traces
No silent fallback when Ollama or a model is unavailable
All actions execute in software simulation. The operator retains field authority
Notes: Evidence: results/live_study_summary.json and results/llama_transcript.json in the v2 bundle. Actual local Ollama calls and OpenDSS simulations. The companion bundle contains the source subset, executed notebooks, HTML preview, PNG/SVG figures, source code and raw Llama transcripts. Network source: https://data.openei.org/submissions/2981 .